## Slide 1: Innovative Training and Education on Renewable Energy Systems: Towards the Future Resilient, Sustainable and Carbon-Neutral Power Systems
2023 IEEE PES PowerTech Tutorial
25 June 2023

## Slide 2: EMT modelling and simulation of grid-forming converter control

## Slide 3: Matej (UNIZG) to prepare this section (90mins)

## Slide 4: About me
Jan 2017 – May 2023: Research and teaching assistant at UNIZG FER
July 2023 – : Project engineer at HVDC System Performance Department, Hitachi Energy
Primary research area: Frequency dynamics of low-inertia systems and model order reduction for system frequency response studies
Contact: matej.krpan@fer.hr

## Slide 5: About the tutorial
Significant penetration of converter-interfaced devices (CID)
Grid-forming voltage source converters (VSCs): one of the solutions for enabling high share of RES/CID
EMT simulations might be required for specific power system studies in the future
Source: P. Tielens and D. Van Hertem, “The relevance of inertia in power systems,” Renew. Sustain. Energy Rev., vol. 55, pp. 999–1009, 2016.

## Slide 6: About the tutorial
For beginners
Basic understanding of RMS/EMT simulations
EMT average model of a VSC controlled as a VSM (virtual synchronous machine)
Commercial power system analysis software (PowerFactory 2022 SP4)
Material will be available

## Slide 7: Refresher course
RMS | EMT
Grid dynamics neglected (phasors) | Grid dynamics considered (differential equations)
Algebraic equations: machine stator, transformers, lines, shunt elements | Algebraic equations: -
Diff. equations: machine rotor, control systems | Diff. equations: Everything
Step size: 1 – 10 ms, bulk systems | Step size: 1 – 100 s, small systems

## Slide 8: Refresher course
RMS | EMT
Domain: real-imaginary | Domain: abc

## Slide 9: Refresher course
Switching EMT models | Averaged EMT models
Models VSC with semiconductor switches | Models VSC as a controlled voltage source at fundamental frequency
Requires step size | Enables larger step size
Switching EMT models | Averaged EMT models
Models VSC with semiconductor switches | Models VSC as a controlled voltage source at fundamental frequency
 | Enables larger step size

## Slide 10: Let’s get started
Choosing the size of the converter
Per-unit base values
AC filter design
Control system design + Model initialization
Time-domain simulations

## Slide 11: Choosing the size of the converter
Choosing the size of the converter
Per-unit base values
AC filter design
Control system design + Model initialization
Time-domain simulations

## Slide 12: Choosing the size of the converter
Arbitrary
100 MVA converter
400 kV point of common coupling (PCC)
Connection to an infinite bus one 100 km 400 kV overhead line

## Slide 13: Choosing the size of the converter

## Slide 14: Per-unit base values
Choosing the size of the converter
Per-unit base values
AC filter design
Control system design + Model initialization
Time-domain simulations

## Slide 15: Per-unit base values
We have both AC and DC quantities
Careful selection of base values to be mathematically consistent
We will use line-to-neutral peak values of AC side quantities

## Slide 16: Per-unit base values
VSC nominal power: MVA
VSC nominal voltage: kV (RMS line-to-line)
Base AC power: MVA
Base AC voltage: kV (peak line-to-neutral)
Base AC current: A (peak line current)
Base AC frequency: rad/s
Base AC impedance: 

## Slide 17: Per-unit base values
Base AC inductance: H
Base AC capacitance: F
Base DC power: MVA
Base AC voltage: kV (to obtain 1 p.u. AC voltage at unity modulation)
kV

## Slide 18: Per-unit base values
Base DC current: A
Base DC impedance: 
Base DC capacitance:
Base DC inductance: H

## Slide 19: AC filter design
Choosing the size of the converter
Per-unit base values
AC filter design
Control system design + Model initialization
Time-domain simulations

## Slide 20: AC filter design
Back-of-the-envelope guide:
Let’s say we want our VSC to have a closed-loop time constant ms ( ms)
Bandwidth is then rad/s  Hz.
Set H
Set such that under , e.g., F
Calculate resonant frequency rad/s, Hz
Check that : 
Set damping resistor ; Losses MW p.u. 

## Slide 21: AC filter design
If everything was done correctly, usual values are:

## Slide 22: AC filter design

## Slide 23: Control system design
Choosing the size of the converter
Per-unit base values
AC filter design
Control system design + Model initialization
Time-domain simulations

## Slide 24: Composite model frame
First we need to create a Composite Model Frame
To define slots with inputs and outputs for internal controllers and elements
To define signal routing between different elements of the control system
Created inside Project > Library > Dynamic models or Project > Library > User defined models

## Slide 25: Composite model frame

## Slide 26: Composite model frame

## Slide 27: Composite model frame
SLOT | DESCRIPTION | CLASS | INPUTS | OUTPUTS
Converter | Static generator element in the grid | *ElmGenstat | u1r_in, u1i_in | 
dq  αβ0 transformation |  | *ElmDsl | udref, uqref, theta | uref_alpha, uref_beta
abc  dq0 transformation |  | *ElmDsl | theta, uf_A; uf_B; uf_C, ic_A; ic_B; ic_C, ig_A; ig_B; ig_C | igd; igq, ufd; ufq, icd; icq
Device level control | Outer voltage / inner current control loops | *ElmDsl | udrefi,uqrefi, dud,duq,igd;igq, ufd;ufq,icd;icq, f,vdc | udref, uqref
System level control – Active power control | VSM emulation | *ElmDsl | pref, p, f_pll, theta_pll | f, theta
System level control – AC voltage control | Voltage reference with Q droop and threshold virtual impedance | *ElmDsl | qref, q, f, icd; icq | udrefi, uqrefi, dud, duq

## Slide 28: Composite model frame
SLOT | DESCRIPTION | CLASS | INPUTS | OUTPUTS
DC voltage control | DC link voltage control | *ElmDsl | vdcref, vdc, pext | pextref
Plant dynamics | External plant dynamics model | *ElmDsl | pextref | pext
DC link dynamics | DC link dynamics | *ElmDsl | pc,pext | vdc
PLL | Phase-locked loop | *ElmPhi__pll |  | fmeas, x2 (theta_pll)
Power measurement - converter | PQ measurement device | *StaPqmea |  | P
Power measurement - grid | PQ measurement device | *StaPqmea |  | P, q

## Slide 29: Composite model frame
SLOT | DESCRIPTION | CLASS | INPUTS | OUTPUTS
Filter voltage measurement |  | *StaVmea |  | u_A;u_B;u_C
Converter current measurement |  | *StaImea |  | i_A;i_B;i_C
Grid current measurement |  | *StaImea |  | i_A;i_B;i_C

## Slide 30: DSL model types
Now we can define the DSL model types that will go inside the slots
Internal structure of the controllers
Names of slots’ input/output variables MUST MATCH the names of input/output variables in DSL model types (case sensitive)
Created inside Project > Library > Dynamic models or Project > Library > User defined models
Can be created from the toolbar via Insert > Dynamic models > DSL model type

## Slide 31: DSL model types

## Slide 32: dq  αβ0 transformation

## Slide 33: dq  αβ0 transformation
Inverse Park transform
Static generator element takes α and β voltage components as inputs

## Slide 34: dq  αβ0 transformation

## Slide 35: dq  αβ0 transformation

## Slide 36: dq  αβ0 transformation

## Slide 37: dq  αβ0 transformation

## Slide 38: abc  dq0 transformation
Park transform
VSC control in a synchronous reference frame rotating at the speed of the VSM
Power-variant transform

## Slide 39: abc  dq0 transformation

## Slide 40: abc  dq0 transformation

## Slide 41: abc  dq0 transformation

## Slide 42: abc  dq0 transformation

## Slide 43: abc  dq0 transformation
! Functionality: This macro implements the power variant forward Park transformatopm (a,b,c)->(d,q)
! It aligns phase a to the d-axis.
! Supports EMT simulation only.
d = 2/3*( cos(theta)*a +cos(theta-twopi()/3)*b+cos(theta+twopi()/3)*c)
q = 2/3*(-sin(theta)*a -sin(theta-twopi()/3)*b-sin(theta+twopi()/3)*c)
inc(d) = 2/3*( cos(theta)*a +cos(theta-twopi()/3)*b+cos(theta+twopi()/3)*c)
inc(q) = 2/3*(-sin(theta)*a -sin(theta-twopi()/3)*b-sin(theta+twopi()/3)*c)

## Slide 44: SRF voltage and current controller

## Slide 45: SRF voltage and current controller

## Slide 46: SRF voltage and current controller

## Slide 47: SRF voltage and current controller

## Slide 48: System level control – Active power control

## Slide 49: System level control – Active power control

## Slide 50: System level control – Active power control

## Slide 51: System level control – Active power control

## Slide 52: System level control – Active power control
inc(xspeed) = 1.0
inc(xtheta) = theta_pll
inc(theta) = xtheta
inc(f) = xspeed
inc0(pref) = p

## Slide 53
Sets the voltage reference for internal controller
Implements droop on reactive power
Implements virtual impedance for limiting transient overcurrents
Threshold virtual impedance [4,6] is used instead of conventional VI for better performance during faults
Rv and Lv are calculated as a function of converter current magnitude
Active only when
System level control – AC voltage control

## Slide 54
System level control – AC voltage control

## Slide 55
System level control – AC voltage control

## Slide 56
System level control – AC voltage control

## Slide 57
System level control – AC voltage control

## Slide 58: DC link
Based on power equation instead of current equation

## Slide 59: DC link

## Slide 60: DC link

## Slide 61: DC link

## Slide 62: DC voltage control

## Slide 63: DC voltage control

## Slide 64: DC voltage control

## Slide 65: Plant dynamics

## Slide 66: Plant dynamics

## Slide 67: Plant dynamics

## Slide 68: Measurement devices
Filter voltage measurement
Converter power measurement
Converter current measurement
Grid power measurement
Grid current measurement

## Slide 69: Grid power measurement

## Slide 70: Converter power measurement

## Slide 71: Filter voltage measurement

## Slide 72: Converter current measurement

## Slide 73: Grid current measurement
RMS value of base current due to the way PF handles quantities

## Slide 74: Model initialization
Generally, output-to-input
Sometimes input-to-output and potential deadlocks need to be taken care of
Load flow will initialize Static generator input variables u1r_in, u1i_in
Load flow will initialize voltages, currents and PLL phase angle measurements
Internal VSM angle theta is the output of the VSM slot initialized manually

## Slide 75: Model initializaton

## Slide 76: Model initializaton

## Slide 77: Controller tuning
Inner current control loop is tuned based on such that the closed-loop system behaves as a first-order transfer function with desired time constant
Outer voltage control loop tuned based on such that the bandwidth is of the current loop bandwidth
PLL bandwidth between 10 and 200 rad/s. Must be high enough to track frequency sufficiently quickly, but low enough to filter out high-frequency EMT voltage disturbances
DC control bandwidth between 1/10 and 1/5 of the inner loop bandwidth (it can be faster in this particular case since it is decoupled from the AC current/voltage control)

## Slide 78: Current controller
        Desired time constant ms
        (Bandwidth = rad/s
        p.u
        p.u

## Slide 79: Voltage controller
        Desired time constant ms
        Inner loop bandwidth rad/s
        Outer loop bandwidth rad/s
– Desired damping

## Slide 80: Voltage controller
        Performance and tuning strongly depends on grid-connected or isolated model of operation
        Grid-connected: Disable voltage feed-forward at the output of inner current controller (ffv = 0)
Isolated mode: Enable voltage feed-forward at the output of inner current controller (ffv = 1) and retune Kp and Ki to take into account line capacitance if significant
        p.u.

## Slide 81: PLL controller
        For closed-loop bandwidth rad/s and (arbitrary values):

## Slide 82: PLL controller
        PLL frequency tracking performance to a step change of infinite bus frequency

## Slide 83: DC controller and DC link
        For closed-loop bandwidth rad/s and (arbitrary values):

## Slide 84: DC controller and DC link
        DC voltage reference tracking

## Slide 85: Time-domain simulation setup

## Slide 86: Time-domain simulation setup

## Slide 87: Time-domain simulation setup

## Slide 88: Grid-connected: Power reference tracking

## Slide 89: Grid-connected: 3PH short-circuit at 50%

## Slide 90: Loss of external grid (Transition to island mode)

## Slide 91: Isolated mode: Load increase

## Slide 92: Isolated mode: Voltage reference increase
Slow and poor tracking because the controller was tuned to the grid-connected operation

## Slide 93: Isolated mode: Voltage reference increase
Enabling PCC voltage feed-forward in current control
Retuning Kp and Ki of voltage controller to consider Cline

## Slide 94: Final remarks
        Make sure you are consistent with mathematical transformations (per-unit, dq orientation, line/phase + peak/rms values, current and power directions)
        Sensitivity of grid-forming control to short-circuit faults: standard current reference saturation can result in instability
        All the control system are applicable to other grid-forming controls (droop, synchronverter, etc.)
        DC link dynamics have no effect in the presented averaged model – grid-forming synchronization based on DC link imbalance requires appropriate design

## Slide 95: Literature
        B. Barac, M. Krpan, T. Capuder, and I. Kuzle, “Modeling and Initialization of a Virtual Synchronous Machine for Power System Fundamental Frequency Simulations,” IEEE Access, vol. 9, pp. 160116–160134, 2021, doi: 10.1109/ACCESS.2021.3130375.
        S. D’Arco, J. A. Suul, and O. B. Fosso, “A Virtual Synchronous Machine implementation for distributed control of power converters in SmartGrids,” Electric Power Systems Research, vol. 122, pp. 180–197, May 2015, doi: 10.1016/J.EPSR.2015.01.001.
        M. Krpan, I. Erceg, I. Kuzle, and H. Pandzic, “Three-Phase SRF PLL Model for System Frequency Response Studies in Low-Inertia Systems,” in 2022 IEEE PES Innovative Smart Grid Technologies - Asia (ISGT Asia), IEEE, Nov. 2022, pp. 155–159. doi: 10.1109/ISGTASIA54193.2022.10003520.
        G. Denis, T. Prevost, M. S. Debry, F. Xavier, X. Guillaud, and A. Menze, “The migrate project: The challenges of operating a transmission grid with only inverter-based generation. A grid-forming control improvement with transient current-limiting control,” IET Renewable Power Generation, vol. 12, no. 5, pp. 523–529, Apr. 2018, doi: 10.1049/IET-RPG.2017.0369/CITE/REFWORKS.
        G. Denis, T. Prevost, P. Panciatici, X. Kestelyn, F. Colas and X. Guillaud, "Improving robustness against grid stiffness, with internal control of an AC voltage-controlled VSC," 2016 IEEE Power and Energy Society General Meeting (PESGM), Boston, MA, USA, 2016, pp. 1-5, doi: 10.1109/PESGM.2016.7741341.
        A. D. Paquette and D. M. Divan, "Virtual Impedance Current Limiting for Inverters in Microgrids With Synchronous Generators," in IEEE Transactions on Industry Applications, vol. 51, no. 2, pp. 1630-1638, March-April 2015, doi: 10.1109/TIA.2014.2345877.
        A. Yazdani and R. Iravani, Voltage-sourced converters in power systems: modeling, control, and applications. John Wiley & Sons, 2010.
        M. Liserre, F. Blaabjerg, and S. Hansen, “Design and control of an LCL-filter-based three-phase active rectifier,” IEEE Transactions on Industry Applications, vol. 41, no. 5, pp. 1281–1291, Sep. 2005, doi: 10.1109/TIA.2005.853373.
        M. Liserre, F. Blaabjerg, and A. Dell’aquila, “Step-by-step design procedure for a grid-connected three-phase PWM voltage source converter,” http://dx.doi.org/10.1080/00207210412331306186, vol. 91, no. 8, pp. 445–460, Aug. 2007, doi: 10.1080/00207210412331306186.
        P. Channegowda and V. John, “Filter Optimization for Grid Interactive Voltage Source Inverters,” IEEE Transactions on Industrial Electronics, vol. 57, no. 12, pp. 4106–4114, Dec. 2010, doi: 10.1109/TIE.2010.2042421.

## Slide 96: Material and info
        PowerFactory model:
        https://applygit.zvne.fer.hr/mkrpan/powertech-belgrade-tutorial-vsm.git
        E-mail:
        matej.krpan@fer.hr